# System Narrative — Evoqua Vantage M284R RO Unit

## 1. Project Overview

This document describes the operation of the Evoqua Water Technologies Vantage® M284R-044 two-pass reverse osmosis (RO) unit installed at the Electric Hydrogen facility in Beaumont, TX (Evoqua Project 2034/001845). The unit is designed to produce 100 GPM of high-purity RODI water for electrolyzer feedwater supply.

## 2. Feed Water

Feed water is drawn from a deep well source (conductivity ~1276 µS/cm, pH 6.31, turbidity 57.4 NTU). The feed passes through pre-treatment prior to reaching the RO skid. Minimum inlet pressure is 30 psig.

## 3. Flow Measurement

Three Georg Fischer Signet 3-2537-6C-P0 paddlewheel flow transmitters monitor system performance. FT-301 measures 1st-pass feed flow (target 128 GPM). FT-303 measures 2nd-pass product flow (target 100 GPM). Flow signals feed the Siemens S7-1215C PLC for recovery calculation and low-flow shutdown. All three transmitters share part number 3-2537-6C-P0.

## 4. Pressure Monitoring

High-pressure transmitters monitor pump discharge pressure in both passes. PIT-305 (0–1450 psi, IFM Efector PN2292) monitors 1st-pass pump discharge and triggers high-pressure shutdown at the configured setpoint. PIT-312 provides the equivalent function on the 2nd-pass pump. Both transmitters output 4-20 mA to the PLC.

## 5. Level Protection — Pump Suction

Three Grundfos rigid suction lance level alarms (p/n 98071114) protect the feed pumps from dry-run damage. LSL-201 is mounted at the minimum suction level on the first-stage pump. When the suction level falls below the switch setpoint, the PLC initiates an immediate shutdown to prevent pump cavitation. LSL-202 and LSL-203 provide the same protection on subsequent pump stages.

## 6. RODI Buffer Tank

RO product water is stored in the RODI buffer tank before delivery to the electrolyzer. LIT-501 (Rosemount 3051L, ±250 inH₂O differential pressure transmitter) provides continuous level monitoring with 4-20 mA output to the PLC. High-level standby: when LIT-501 indicates full tank, the RO enters standby mode and flushes periodically. HV-507 (Bray 4" 175 PSI butterfly valve) is the primary isolation valve on the tank outlet supply to the electrolyzer feed header. An N2 blanket (PCV-500) maintains tank pressure and a conservation vent (CBV-501) prevents over/under-pressure conditions.

## 7. Control System

The unit is controlled by a Siemens S7-1215C PLC with a Siemens TP700 Comfort Panel HMI. All instruments communicate via 4-20 mA analog signals to the PLC I/O cards. Shutdown alarms include: high product conductivity, low feed pressure, low feed flow, high product pressure, high pump discharge pressure, and high feed water temperature. Ethernet connectivity is provided for remote SCADA integration.